## Sheet1
Unit Water Produced, kW-h/m3
WSCs | 2012 | 2013 | 2014 | 2015 | 2016 | Average
Anshan | 0.37956 | 0.36083 | 0.322 | 0.3151 | 0.30882 | 0.33726
Fushun | 0.42158 | 0.43142 | 0.42173 | 0.3873 | 0.36828 | 0.40606
Fuxin | 0.7083 | 0.6769 | 0.68391 | 0.6901 | 0.70091 | 0.69202
Gaizhou | 0.38186 | 0.41134 | 0.43729 | 0.36981 | 0.40255 | 0.40057
Shenyang | 0.60587 | 0.60981 | 0.55912 | 0.52716 | 0.51471 | 0.56333
Unit Electricity Fees, RMB/kW-h
WSCs | 2012 | 2013 | 2014 | 2015 | 2016 | Average
Anshan | 0.74474 | 0.7265 | 0.72543 | 0.7075 | 0.64007 | 0.70885
Fushun | 0.6627 | 0.66004 | 0.65427 | 0.65396 | 0.65028 | 0.65625
Fuxin | 0.76494 | 0.78713 | 0.75724 | 0.76537 | 0.67538 | 0.75001
Gaizhou | 0.8 | 0.8 | 0.8 | 0.8 | 0.8 | 0.8
Shenyang | 0.73299 | 0.76345 | 0.8087 | 0.66079 | 0.61798 | 0.71678
Electricity Fees to O&M Costs, %
WSCs | 2012 | 2013 | 2014 | 2015 | 2016 | Average
Anshan | 89.8075 | 81.714 | 47.0162 | 40.9719 | 38.1583 | 59.5336
Fushun | 24.1347 | 23.4458 | 23.2901 | 18.3842 | 15.6834 | 20.9876
Fuxin | 65.7934 | 56.5172 | 57.2678 | 57.2867 | 56.2755 | 58.6281
Gaizhou | 59.3024 | 57.816 | 52.38 | 61.9117 | 70.1574 | 60.3135
Shenyang | 63.1163 | 63.5372 | 68.5059 | 60.3361 | 55.6612 | 62.2313

## Sheet2
|  | Anshan Water Supply Company Major Equipment Power Usage, kwH/month | [6 empty] | Average |  | 鞍山自来水公司净水厂主要处理单元能耗需求一览表 - 月均能耗，千瓦小时
|  | Treatment Units / Month-Year | 2015-04-01 | 2015-07-01 | 2015-10-01 | 2016-01-01 | 2016-04-01 | 2016-07-01 |  | Notes | 设备/年度 | 2015.7 | 2015.4 | 2015.10 | 2016.1 | 2016.4 | 2016.7 | Notes
|  | Water Intake Pumping | 1282369 | 1440518 | 1300519 | 1475429 | 1208478 | 1284279 | 1331932 | 2015.4和2016.4是最低 月 | 取水泵 | 1440518 | 1282369 | 1300519 | 1475429 | 1208478 | 1284279 | 2015.4和2016.4是最低 月
|  | Chemical Pumping | 7608 | 10093.6 | 10093.6 | 10093.6 | 9768 | 10093.6 | 9625.0667 |  | 加药泵 | 10093.6 | 7608 | 10093.6 | 10093.6 | 9768 | 10093.6
|  | Sedimentation | 1152 | 2134.08 | 2625.12 | 2625.12 | 2102.4 | 2134.08 | 2128.8 | 2015.7和2016.1是最高 月 | 沉淀 | 2134.08 | 1152 | 2625.12 | 2625.12 | 2102.4 | 2134.08 | 2015.7和2016.1是最高 月
|  | Filtration/Backwash | 5207.58 | 5337.51 | 6384.15 | 6748.5 | 9730.5 | 6713.8 | 6687.0067 |  | 过滤/反冲洗 | 5337.51 | 5207.58 | 6384.15 | 6748.5 | 9730.5 | 6713.8
|  | Disinfection | 2890 | 2986 | 2986 | 2986 | 2890 | 2986 | 2954 | 2015.10和2016.7是最普通月 | 消毒 | 2986 | 2890 | 2986 | 2986 | 2890 | 2986 | 2015.10和2016.7是最普通月
|  | Produced Water Pumping | 732065 | 830866 | 808016 | 880828 | 697367 | 769403 | 786424.1667 |  | 清水泵 | 830866 | 732065 | 808016 | 880828 | 697367 | 769403
|  | Distribution Pumping | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 配水泵 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Power Usage | 2031291.58 | 2291935.19 | 2130623.87 | 2378710.22 | 1930335.9 | 2075609.48 | 2139751.04
Anshan WSC | % of Total | Water Treatment Power Usage | 16857.58 | 20551.19 | 22088.87 | 22453.22 | 24490.9 | 21927.48 | 21394.8733
% Water Treatment of Total Power Usage | 1.005% | % Water Treatment of Total Power Usage | 0.8299% | 0.8967% | 1.037% | 0.9439% | 1.269% | 1.056% | 1.005%
% Water Intake Pumping of Total Power Usage | 62.25% | % Water Intake Pumping of Total Power Usage | 63.13% | 62.85% | 61.04% | 62.03% | 62.6% | 61.87% | 62.25%
% Produced Water Pumping of Total Power Usage | 36.74% | % Produced Water Pumping of Total Power Usage | 36.04% | 36.25% | 37.92% | 37.03% | 36.13% | 37.07% | 36.74%
| 100% | Note: two largest WSPs of the Anshan WSC
|  | Fushun Water Supply Company Major Equipment Power Usage, kwH/month | [8 empty] | 抚顺自来水公司净水厂主要处理单元能耗需求一览表 - 月均能耗，万千瓦小时
|  | Treatment Units / Month-Year | 2015-02-01 | 2015-06-01 | 2015-10-01 | 2016-02-01 | 2016-06-01 | 2016-10-01 |  |  | 设备/年度 | 2015.2 | 2015.6 | 2015.10 | 2016.2 | 2016.6 | 2016.10 | 注
|  | Water Intake Pumping | 3041000 | 2445800 | 2024000 | 2152000 | 2046000 | 2083000 | 2298633.3333 |  | 取水泵 | 304.1 | 244.58 | 202.4 | 215.2 | 204.6 | 208.3
|  | Chemical Pumping | 16000 | 11200 | 0 | 12400 | 12600 | 12600 | 10800 |  | 加药泵 | 1.6 | 1.12 | 0 | 1.24 | 1.26 | 1.26
|  | Sedimentation | 0 | 12700 | 0 | 12500 | 12400 | 12400 | 8333.3333 |  | 沉淀 | 0 | 1.27 | 0 | 1.25 | 1.24 | 1.24
|  | Filtration/Backwash | 14000 | 20000 | 14100 | 25600 | 25600 | 25500 | 20800 |  | 过滤/反冲洗 | 1.4 | 2 | 1.41 | 2.56 | 2.56 | 2.55
|  | Disinfection | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 消毒 | 0 | 0 | 0 | 0 | 0 | 0
|  | Produced Water Pumping | 1224000 | 1245500 | 1420700 | 1607000 | 1389300 | 1423000 | 1384916.6667 |  | 清水泵 | 122.4 | 124.55 | 142.07 | 160.7 | 138.93 | 142.3
|  | Distribution Pumping | 211500 | 181100 | 212400 | 196800 | 184400 | 392700 | 229816.6667 |  | 配水泵 | 21.15 | 18.11 | 21.24 | 19.68 | 18.44 | 39.27
|  | Total Power Usage | 4506500 | 3916300 | 3671200 | 4006300 | 3670300 | 3949200 | 3953300
Fushun WSC | % of Total | Water Treatment Power Usage | 30000 | 43900 | 14100 | 50500 | 50600 | 50500 | 39933.3333
% Water Treatment of Total Power Usage | 1.015% | % Water Treatment of Total Power Usage | 0.6657% | 1.121% | 0.3841% | 1.261% | 1.379% | 1.279% | 1.015%
% Water Intake Pumping of Total Power Usage | 57.88% | % Water Intake Pumping of Total Power Usage | 67.48% | 62.45% | 55.13% | 53.72% | 55.74% | 52.74% | 57.88%
% Produced Water Pumping of Total Power Usage | 35.28% | % Produced Water Pumping of Total Power Usage | 27.16% | 31.8% | 38.7% | 40.11% | 37.85% | 36.03% | 35.28%
% Distribution Pumping of Total Power Usage | 5.831% | % Distribution Pumping of Total Power Usage | 4.693% | 4.624% | 5.786% | 4.912% | 5.024% | 9.944% | 5.831%
100%
|  | Fuxin Water Supply Company Major Equipment Power Usage, kwH/month | [8 empty] | 阜新自来水公司净水厂主要处理单元能耗需求一览表 - 月均能耗，万千瓦小时
|  | Treatment Units / Month-Year | 2015-02-01 | 2015-06-01 | 2015-10-01 | 2016-02-01 | 2016-06-01 | 2016-10-01 |  |  | 设备/年度 | 2015.2 | 2015.6 | 2015.10 | 2016.2 | 2016.6 | 2016.10 | 注
|  | Water Intake Pumping | 1049574 | 666775 | 931526 | 1255436 | 923941 | 732668 | 926653.3333 |  | 取水泵 | 104.9574 | 66.6775 | 93.1526 | 125.5436 | 92.3941 | 73.2668 |  | 3275 | 2803 | 2547 | 3678 | 2848 | 2527
|  | Chemical Feed Pumping | 3275 | 2803 | 2547 | 3678 | 2848 | 2527 | 2946.3333 |  | 加药泵 | 0.5745 | 0.5745 | 0.5745 | 0.5745 | 0.5745 | 0.5745 |  | 60014 | 47433 | 46472 | 67071 | 49877 | 43964
|  | Sedimentation | 60014 | 47433 | 46472 | 67071 | 49877 | 43964 | 52471.8333 |  | 沉淀 | 9.4553 | 9.4553 | 9.4553 | 9.4553 | 9.4553 | 9.4553 |  | 2929 | 2671 | 2966 | 3372 | 2922 | 2659
|  | Filtration/Backwash | 2929 | 2671 | 2966 | 3372 | 2922 | 2659 | 2919.8333 |  | 过滤/反冲洗 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 | 0.72 |  | 1649 | 1591 | 1684 | 1905 | 1701 | 1554
|  | Disinfection | 1649 | 1591 | 1684 | 1905 | 1701 | 1554 | 1680.6667 |  | 消毒 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432 | 0.432
|  | Produced Water Pumping | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 清水泵 | 164.9411 | 172.7177 | 123.9726 | 188.366 | 134.4286 | 139.7208 |  | 750812 | 891139 | 414686 | 858078 | 552262 | 670537
|  | Distribution Pumping | 750812 | 891139 | 414686 | 858078 | 552262 | 670537 | 689585.6667 |  | 配水泵 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Power Usage | 1868253 | 1612412 | 1399881 | 2189540 | 1533551 | 1453909 | 1676257.6667
Fuxin WSC | % of Total | Water Treatment Power Usage | 67867 | 54498 | 53669 | 76026 | 57348 | 50704 | 60018.6667
% Water Treatment of Total Power Usage | 3.591% | % Water Treatment of Total Power Usage | 3.633% | 3.38% | 3.834% | 3.472% | 3.74% | 3.487% | 3.591%
% Water Intake Pumping of Total Power Usage | 55.34% | % Water Intake Pumping of Total Power Usage | 56.18% | 41.35% | 66.54% | 57.34% | 60.25% | 50.39% | 55.34%
% Produced Water Pumping of Total Power Usage | 41.07% | % Produced Water Pumping of Total Power Usage | 40.19% | 55.27% | 29.62% | 39.19% | 36.01% | 46.12% | 41.07%
| 100% | Note: no electric meters for water treatment units, so power usages are estimated per equipment nominal power requirements
|  | Gaizhou Water Supply Company Major Equipment Power Usage, kwH/month | [8 empty] | 盖州自来水公司净水厂主要处理单元能耗需求一览表 - 月均能耗，万千瓦小时
|  | Treatment Units / Month-Year | 2015-01-01 | 2015-04-01 | 2015-08-01 | 2016-01-01 | 2016-04-01 | 2016-08-01 |  |  | 设备/年度 | 2015.1 | 2015.4 | 2015.8 | 2016.1 | 2016.4 | 2016.8 | 注
|  | Water Intake Pumping | 121520 | 111720 | 120912 | 112406 | 114660 | 115444 | 116110.3333 |  | 取水泵 | 12.152 | 11.172 | 12.0912 | 11.2406 | 11.466 | 11.5444
|  | Chemical Pumping | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 加药泵 | 0 | 0 | 0 | 0 | 0 | 0
|  | Sedimentation | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 沉淀 | 0 | 0 | 0 | 0 | 0 | 0
|  | Filtration/Backwash | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 过滤/反冲洗 | 0 | 0 | 0 | 0 | 0 | 0
|  | Disinfection | 3240 | 3200 | 3240 | 3105 | 3215 | 3186 | 3197.6667 |  | 消毒 | 0.324 | 0.32 | 0.324 | 0.3105 | 0.3215 | 0.3186
|  | Produced Water Pumping | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 清水泵 | 0 | 0 | 0 | 0 | 0 | 0
|  | Distribution Pumping | 122221 | 124628 | 122833 | 132441 | 122315 | 129795 | 125705.5 |  | 配水泵 | 12.2221 | 12.4628 | 12.2833 | 13.2441 | 12.2315 | 12.9795
|  | Total Power Usage | 246981 | 239548 | 246985 | 247952 | 240190 | 248425 | 245013.5
Gaizhou WSC | % of Total | Water Treatment Power Usage | 3240 | 3200 | 3240 | 3105 | 3215 | 3186 | 3197.6667
% Water Treatment of Total Power Usage | 1.305% | % Water Treatment of Total Power Usage | 1.312% | 1.336% | 1.312% | 1.252% | 1.339% | 1.282% | 1.305%
% Water Intake Pumping of Total Power Usage | 47.39% | % Water Intake Pumping of Total Power Usage | 49.2% | 46.64% | 48.96% | 45.33% | 47.74% | 46.47% | 47.39%
% Produced Water Pumping of Total Power Usage | 0% | % Produced Water Pumping of Total Power Usage | [6 empty] | 0% | bar: 2015-01-01 to 2016-08-01
% Distribution Pumping of Total Power Usage | 51.31% | % Distribution Pumping of Total Power Usage | 49.49% | 52.03% | 49.73% | 53.41% | 50.92% | 52.25% | 51.31%
| 100% | Note: groundwater is extracted and only disinfection required before serving customers
|  | Shenyang Water Supply Company Major Equipment Power Usage, kwH/month | [8 empty] | 沈阳自来水公司净水厂主要处理单元能耗需求一览表 - 月均能耗，万千瓦小时
|  | Treatment Units / Month-Year | 2014-02-01 | 2014-06-01 | 2014-10-01 | 2016-02-01 | 2016-06-01 | 2016-10-01 |  |  | 设备/年度 | 2015.2 | 2015.6 | 2015.10 | 2016.2 | 2016.6 | 2016.10
|  | Water Intake Pumping | 528000 | 443000 | 490000 | 548000 | 460000 | 403000 | 478666.6667 |  | 取水泵 | 52.8 | 44.3 | 49 | 54.8 | 46 | 40.3
|  | Chemical Pumping | 6335 | 6336 | 6336 | 6335 | 6336 | 6336 | 6335.6667 |  | 加药泵 | 0.6335 | 0.6336 | 0.6336 | 0.6335 | 0.6336 | 0.6336
|  | Sedimentation | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 沉淀 | 0 | 0 | 0 | 0 | 0 | 0
|  | Filtration/Backwash | 28750 | 28750 | 28630 | 28630 | 28630 | 28640 | 28671.6667 |  | 过滤/反冲洗 | 2.875 | 2.875 | 2.863 | 2.863 | 2.863 | 2.864
|  | Disinfection | 183 | 182 | 183 | 182 | 180 | 180 | 181.6667 |  | 消毒 | 0.0183 | 0.0182 | 0.0183 | 0.0182 | 0.018 | 0.018
|  | Produced Water Pumping | 2653000 | 2363000 | 2526000 | 2555000 | 2351000 | 2503000 | 2491833.3333 |  | 清水泵 | 265.3 | 236.3 | 252.6 | 255.5 | 235.1 | 250.3
|  | Distribution Pumping | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Power Usage | 3216268 | 2841268 | 3051149 | 3138147 | 2846146 | 2941156 | 3005689
Shenyang WSC | % of Total | Water Treatment Power Usage | 35268 | 35268 | 35149 | 35147 | 35146 | 35156 | 35189 |  |  | 528000 | 443000 | 490000 | 548000 | 460000 | 403000
% Water Treatment of Total Power Usage | 1.173% | % Water Treatment of Total Power Usage | 1.097% | 1.241% | 1.152% | 1.12% | 1.235% | 1.195% | 1.173% |  |  | 6335 | 6336 | 6336 | 6335 | 6336 | 6336
% Water Intake Pumping of Total Power Usage | 15.9% | % Water Intake Pumping of Total Power Usage | 16.42% | 15.59% | 16.06% | 17.46% | 16.16% | 13.7% | 15.9%
% Produced Water Pumping of Total Power Usage | 82.93% | % Produced Water Pumping of Total Power Usage | 82.49% | 83.17% | 82.79% | 81.42% | 82.6% | 85.1% | 82.93%
| 100% | Note: only one surface water treatment plant, the No. 8 WSP | [9 empty] | 0 | 0 | 0 | 0 | 0 | 0
[12 empty] | 28750 | 28750 | 28630 | 28630 | 28630 | 28640
[12 empty] | 183 | 182 | 183 | 182 | 180 | 180
[12 empty] | 2653000 | 2363000 | 2526000 | 2555000 | 2351000 | 2503000
Anshan Water Supply Company Major Equipment Power Usage 鞍山水公司主要设备能耗汇整，kwH/月
|  | Treatment Units 处理单位 / 年-月 | 2015-04-01 | 2015-07-01 | 2015-10-01 | 2016-01-01 | 2016-04-01 | 2016-07-01
|  | Water Intake Pumping 取水泵 | 1282369 | 1440518 | 1300519 | 1475429 | 1208478 | 1284279
|  | Chemical Pumping 加压泵 | 7608 | 10093.6 | 10093.6 | 10093.6 | 9768 | 10093.6
|  | Sedimentation 沉淀 | 1152 | 2134.08 | 2625.12 | 2625.12 | 2102.4 | 2134.08
|  | Filtration/Backwash 过滤/反冲洗 | 5207.58 | 5337.51 | 6384.15 | 6748.5 | 9730.5 | 6713.8
|  | Disinfection 消毒 | 2890 | 2986 | 2986 | 2986 | 2890 | 2986
|  | Produced Water Pumping 造水泵 | 732065 | 830866 | 808016 | 880828 | 697367 | 769403
|  | Distribution Pumping 配水泵 | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Power Usage 总能耗 | 2031291.58 | 2291935.19 | 2130623.87 | 2378710.22 | 1930335.9 | 2075609.48
|  | Water Treatment Power Usage 水处理能耗 | 16857.58 | 20551.19 | 22088.87 | 22453.22 | 24490.9 | 21927.48
|  | % 水处理能耗 / 总能耗 | 0.8299% | 0.8967% | 1.037% | 0.9439% | 1.269% | 1.056%
|  | % 取水泵能耗 / 总能耗 | 63.13% | 62.85% | 61.04% | 62.03% | 62.6% | 61.87%
|  | % 造水泵能耗 / 总能耗 | 36.04% | 36.25% | 37.92% | 37.03% | 36.13% | 37.07%
Fushun Water Supply Company Major Equipment Power Usage 抚顺水公司主要设备能耗汇整，kwH/月
|  | Treatment Units 处理单位 / 年-月 | 2015-02-01 | 2015-06-01 | 2015-10-01 | 2016-02-01 | 2016-06-01 | 2016-10-01
|  | Water Intake Pumping 取水泵 | 3041000 | 2445800 | 2024000 | 2152000 | 2046000 | 2083000
|  | Chemical Pumping 加压泵 | 16000 | 11200 | 0 | 12400 | 12600 | 12600
|  | Sedimentation 沉淀 | 0 | 12700 | 0 | 12500 | 12400 | 12400
|  | Filtration/Backwash 过滤/反冲洗 | 14000 | 20000 | 14100 | 25600 | 25600 | 25500
|  | Disinfection 消毒 | 0 | 0 | 0 | 0 | 0 | 0
|  | Produced Water Pumping 造水泵 | 1224000 | 1245500 | 1420700 | 1607000 | 1389300 | 1423000
|  | Distribution Pumping 配水泵 | 211500 | 181100 | 212400 | 196800 | 184400 | 392700
|  | Total Power Usage 总能耗 | 4506500 | 3916300 | 3671200 | 4006300 | 3670300 | 3949200
|  | Water Treatment Power Usage 水处理能耗 | 30000 | 43900 | 14100 | 50500 | 50600 | 50500
|  | % 水处理能耗 / 总能耗 | 0.6657% | 1.121% | 0.3841% | 1.261% | 1.379% | 1.279%
|  | % 取水泵能耗 / 总能耗 | 67.48% | 62.45% | 55.13% | 53.72% | 55.74% | 52.74%
|  | % 造水泵能耗 / 总能耗 | 27.16% | 31.8% | 38.7% | 40.11% | 37.85% | 36.03%
|  | % 配水泵能耗 / 总能耗 | 4.693% | 4.624% | 5.786% | 4.912% | 5.024% | 9.944%
Fuxin Water Supply Company Major Equipment Power Usage 阜新水公司主要设备能耗汇整，kwH/月
|  | Treatment Units 处理单位 / 年-月 | 2015-02-01 | 2015-06-01 | 2015-10-01 | 2016-02-01 | 2016-06-01 | 2016-10-01
|  | Water Intake Pumping 取水泵 | 1049574 | 666775 | 931526 | 1255436 | 923941 | 732668
|  | Chemical Pumping 加压泵 | 3275 | 2803 | 2547 | 3678 | 2848 | 2527
|  | Sedimentation 沉淀 | 60014 | 47433 | 46472 | 67071 | 49877 | 43964
|  | Filtration/Backwash 过滤/反冲洗 | 2929 | 2671 | 2966 | 3372 | 2922 | 2659
|  | Disinfection 消毒 | 1649 | 1591 | 1684 | 1905 | 1701 | 1554
|  | Produced Water Pumping 造水泵 | 0 | 0 | 0 | 0 | 0 | 0
|  | Distribution Pumping 配水泵 | 750812 | 891139 | 414686 | 858078 | 552262 | 670537
|  | Total Power Usage 总能耗 | 1868253 | 1612412 | 1399881 | 2189540 | 1533551 | 1453909
|  | Water Treatment Power Usage 水处理能耗 | 67867 | 54498 | 53669 | 76026 | 57348 | 50704
|  | % 水处理能耗 / 总能耗 | 3.633% | 3.38% | 3.834% | 3.472% | 3.74% | 3.487%
|  | % 取水泵能耗 / 总能耗 | 56.18% | 41.35% | 66.54% | 57.34% | 60.25% | 50.39%
|  | % 造水泵能耗 / 总能耗 | 40.19% | 55.27% | 29.62% | 39.19% | 36.01% | 46.12%
Gaizhou Water Supply Company Major Equipment Power Usage 盖州水公司主要设备能耗汇整，kwH/月
|  | Treatment Units / Month-Year | 2015-01-01 | 2015-04-01 | 2015-08-01 | 2016-01-01 | 2016-04-01 | 2016-08-01
|  | Water Intake Pumping | 121520 | 111720 | 120912 | 112406 | 114660 | 115444
|  | Chemical Pumping | 0 | 0 | 0 | 0 | 0 | 0
|  | Sedimentation | 0 | 0 | 0 | 0 | 0 | 0
|  | Filtration/Backwash | 0 | 0 | 0 | 0 | 0 | 0
|  | Disinfection | 3240 | 3200 | 3240 | 3105 | 3215 | 3186
|  | Produced Water Pumping | 0 | 0 | 0 | 0 | 0 | 0
|  | Distribution Pumping | 122221 | 124628 | 122833 | 132441 | 122315 | 129795
|  | Total Power Usage | 246981 | 239548 | 246985 | 247952 | 240190 | 248425
|  | Water Treatment Power Usage | 3240 | 3200 | 3240 | 3105 | 3215 | 3186
|  | % Water Treatment of Total Power Usage | 1.312% | 1.336% | 1.312% | 1.252% | 1.339% | 1.282%
|  | % Water Intake Pumping of Total Power Usage | 49.2% | 46.64% | 48.96% | 45.33% | 47.74% | 46.47%
% Produced Water Pumping of Total Power Usage | bar: 2015-01-01 to 2016-08-01
|  | % Distribution Pumping of Total Power Usage | 49.49% | 52.03% | 49.73% | 53.41% | 50.92% | 52.25%
Shenyang Water Supply Company Major Equipment Power Usage 沈阳水公司主要设备能耗汇整，kwH/月
|  | Treatment Units / Month-Year | 2014-02-01 | 2014-06-01 | 2014-10-01 | 2016-02-01 | 2016-06-01 | 2016-10-01
|  | Water Intake Pumping | 528000 | 443000 | 490000 | 548000 | 460000 | 403000
|  | Chemical Pumping | 6335 | 6336 | 6336 | 6335 | 6336 | 6336
|  | Sedimentation | 0 | 0 | 0 | 0 | 0 | 0
|  | Filtration/Backwash | 28750 | 28750 | 28630 | 28630 | 28630 | 28640
|  | Disinfection | 183 | 182 | 183 | 182 | 180 | 180
|  | Produced Water Pumping | 2653000 | 2363000 | 2526000 | 2555000 | 2351000 | 2503000
|  | Distribution Pumping | 0 | 0 | 0 | 0 | 0 | 0
|  | Total Power Usage | 3216268 | 2841268 | 3051149 | 3138147 | 2846146 | 2941156
|  | Water Treatment Power Usage | 35268 | 35268 | 35149 | 35147 | 35146 | 35156
|  | % Water Treatment of Total Power Usage | 1.097% | 1.241% | 1.152% | 1.12% | 1.235% | 1.195%
|  | % Water Intake Pumping of Total Power Usage | 16.42% | 15.59% | 16.06% | 17.46% | 16.16% | 13.7%
|  | % Produced Water Pumping of Total Power Usage | 82.49% | 83.17% | 82.79% | 81.42% | 82.6% | 85.1%

## Sheet3
Estimates of NRW Status and Reduction for All WSCs, % |  |  |  | Breakdown of NRW Reduction Targets for All WSCs, %
NRW Reduction via World Bank Loan for Anshan WSC |  |  |  | Categories / WSCs | Anshan | Fushun | Fuxin | Gaizhou | Shenyang |  | 各水公司的产销差降低目标值类别, % | [5 empty] | Breakdown of NRW Reduction Targets for All WSCs, %
Categories/Status | 2016 | Reduction | 2022 | Total NRW | 6.9 | 16.67 | 9.5 | 29 | 3.2 |  | 类别 / 水公司 | 鞍山 | 抚顺 | 阜新 | 盖州 | 沈阳 | Categories / WSCs | Anshan | Fushun | Fuxin | Gaizhou | Shenyang
Total NRW, % | 30.9 | 6.9 | 24 | Transmission Main Loss | 2.4 | 0.37 | 2 | 3 | 1.46 |  | 总产销差 | 6.9 | 16.67 | 9.5 | 29 | 3.2 | Total NRW | 6.41 | 16.36 | 8.68 | 28 | 3.2
Transmission Main Loss | 8.29 | 2.4 | 5.89 | Community Pipeline Loss | 2.1 | 14.75 | 5.11 | 4 | 0.84 |  | 供水管网漏损 | 2.4 | 0.37 | 2 | 3 | 1.46 | Transmission Main Loss | 2.4 | 0.37 | 2 | 3 | 1.46
Community Pipeline Loss | 15.41 | 2.1 | 13.31 | Meter Loss | 0.49 | 0.31 | 0.82 | 1 | 0 |  | 小区管道漏损 | 2.1 | 14.75 | 5.11 | 4 | 0.84 | Community Pipeline Loss | 2.1 | 14.75 | 5.11 | 4 | 0.84
Meter Loss | 1.854 | 0.49 | 1.364 | No-meter Loss | 0 | 0 | 0 | 18 | 0 |  | 有表漏损 | 0.49 | 0.31 | 0.82 | 1 | 0 | Water Supply Loss | 4.5 | 15.12 | 7.11 | 7 | 2.3
No-meter Loss | 0 | 0 | 0 | Management Loss | 0.85 | 1.24 | 1.57 | 3 | 0.9 |  | 无表漏损 | 0 | 0 | 0 | 18 | 0 | Note: “Water Supply Loss” olny considers lossess from transmission main and community pipeline
Management Loss | 3.728 | 0.85 | 2.878 | Others | 1.06 | 0 | 0 | 0 | 0 |  | 管理漏损 | 0.85 | 1.24 | 1.57 | 3 | 0.9
Others | 1.618 | 1.06 | 0.558 | [7 empty] | 其他 | 1.06 | 0 | 0 | 0 | 0
|  |  |  | Water Supply Loss | 4.5 | 15.12 | 7.11 | 7 | 2.3
Water Supply Loss | 23.7 | 4.5 | 19.2 | Note: “Water Supply Loss” olny considers lossess from transmission main and community pipeline | [6 empty] | 供水漏损 | 4.5 | 15.12 | 7.11 | 7 | 2.3
注：供水漏损仅考虑供水管网和小区管道的漏损总和
NRW Reduction via World Bank Loan for Fushun WSC
Categories/Status | 2016 | Reduction | 2022
Total NRW, % | 38.8 | 16.67 | 22.13
Transmission Main Loss | 4.37 | 0.37 | 4
Community Pipeline Loss | 24.74 | 14.75 | 9.99
Meter Loss | 2.29 | 0.31 | 1.98
No-meter Loss | 0 | 0 | 0
Management Loss | 6.97 | 1.24 | 5.73
Others | 0.43 | 0 | 0.43
Water Supply Loss | 29.11 | 15.12 | 13.99
NRW Reduction via World Bank Loan for Fuxin WSC
Categories/Status | 2016 | Reduction | 2022
Total NRW, % | 25.7 | 9.5 | 16.2
Transmission Main Loss | 6.73 | 2 | 4.73
Community Pipeline Loss | 13.51 | 5.11 | 8.4
Meter Loss | 2.46 | 0.82 | 1.64
No-meter Loss | 0 | 0 | 0
Management Loss | 3 | 1.57 | 1.43
Others | 0 | 0 | 0
Water Supply Loss | 20.1 | 7.11 | 11.82
NRW Reduction via World Bank Loan for Gaizhou WSC
Categories/Status | 2016 | Reduction | 2022
Total NRW, % | 64.1 | 29 | 35.1
Transmission Main Loss | 14.1 | 3 | 11.1
Community Pipeline Loss | 12 | 4 | 8
Meter Loss | 5 | 1 | 4 | Water Saving, m3/year | 10338442.5 | 19788957 | 8907200 | 4382190 | 18632753.6 | 51048.64 | 各水公司的节水目标值汇总, m3/年
No-meter Loss | 25 | 18 | 7 | Categories / WSCs | Anshan | Fushun | Fuxin | Gaizhou | Shenyang |  | 类别 / 水公司 | 鞍山 | 抚顺 | 阜新 | 盖州 | 沈阳
Management Loss | 8 | 3 | 5 | Transmission Main Loss | 3595980 | 439227 | 1875200 | 453330 | 8501193.83 | 23290.942 | 供水管网漏损 | 3595980 | 439227 | 1875200 | 453330 | 8501193.83
Others | 0 | 0 | 0 | Community Pipeline Loss | 3146482.5 | 17509725 | 4791136 | 604440 | 4891097.82 | 13400.268 | 小区管道漏损 | 3146482.5 | 17509725 | 4791136 | 604440 | 4891097.82
|  |  |  | Meter Loss | 734179.25 | 368001 | 768832 | 151110 | 0 | 0 | 有表漏损 | 734179.25 | 368001 | 768832 | 151110 | 0
Water Supply Loss | 26.1 | 7 | 19.1 | No-meter Loss | 0 | 0 | 0 | 2719980 | 0 | 0 | 无表漏损 | 0 | 0 | 0 | 2719980 | 0
|  |  |  | Management Loss | 1273576.25 | 1472004 | 1472032 | 453330 | 5240461.95 | 14357.43 | 管理漏损 | 1273576.25 | 1472004 | 1472032 | 453330 | 5240461.95
NRW Reduction via World Bank Loan for Shenyang WSC |  |  |  | Others | 1588224.5 | 0 | 0 | 0 | 0 | 0 | 其他 | 1588224.5 | 0 | 0 | 0 | 0
Categories/Status | 2016 | Reduction | 2022 | Total Water Saving | 10338442.5 | 19788957 | 8907200 | 4382190 | 18632753.6 |  | 总节水 | 10338442.5 | 19788957 | 8907200 | 4382190 | 18632753.6
Total NRW, % | 33 | 3.2 | 29.8
Transmission Main Loss | 14.1 | 1.46 | 12.64 |  | 0.34783 | 0.022196 | 0.21053 | 0.10345 | 0.45625
Community Pipeline Loss | 12.3 | 0.84 | 11.46 |  | 0.30435 | 0.88482 | 0.53789 | 0.13793 | 0.2625
Meter Loss | 2.3 | 0 | 2.3 |  | 0.071014 | 0.018596 | 0.086316 | 0.034483 | 0
No-meter Loss | 0.84 | 0 | 0.84 |  | 0 | 0 | 0 | 0.62069 | 0
Management Loss | 3.46 | 0.9 | 2.56 |  | 0.12319 | 0.074385 | 0.16526 | 0.10345 | 0.28125
Others | 0 | 0 | 0 |  | 0.15362 | 0 | 0 | 0 | 0
[5 empty] | 1 | 1 | 1 | 1 | 1
Water Supply Loss | 26.4 | 2.3 | 24.1
Estimates of Power Usage and Energy Saving for All WSCs, kW-h/month
Energy Saving via World Bank Loan for Anshan WSC |  |  |  | Summary of Energy Saving Targets for All WSCs, kW-h/year | [6 empty] | 各水公司的节能目标值汇总, kW-h/年
Categories/Status | 2016 | Energy Saving | 2022 | Categories / WSCs | Anshan | Fushun | Fuxin | Gaizhou | Shenyang |  | 类别 / 水公司 | 鞍山 | 抚顺 | 阜新 | 盖州 | 沈阳
Total Savinging, kW-h | 2853213 | 207212.35 | 2646000.65 | Water Intake Pumping | 774013.2 | 4109232 | 3456708 | 0 | 0 |  | 取水泵 | 774013.2 | 4109232 | 3456708 | 0 | 0
Water Intake Pumping | 1290022 | 64501.1 | 1225520.9 | Produced Water Pumping | 508695 | 1484268 | 1131624 | 0 | 4043052 |  | 造水泵 | 508695 | 1484268 | 1131624 | 0 | 4043052
Produced Water Pumping | 847825 | 42391.25 | 805433.75 | Distribution Pumping | 50880 | 1032276 | 353604 | 0 | 0 |  | 配水泵 | 50880 | 1032276 | 353604 | 0 | 0
Distribution Pumping | 86045 | 4240 | 81805 | Secondary Booster Pumping | 1152960 | 1701600 | 724560 | 178008 | 1938000 |  | 二级加压泵站 | 1152960 | 1701600 | 724560 | 178008 | 1938000
Secondary Booster Pumping | 629321 | 96080 | 533241 | Others | 0 | 0 | 0 | 0 | 0 |  | 其他 | 0 | 0 | 0 | 0 | 0
Others | 0 | 0 | 0 | Total Energy Saving | 2486548.2 | 8327376 | 5666496 | 178008 | 5981052 |  | 总节能 | 2486548.2 | 8327376 | 5666496 | 178008 | 5981052
Energy Saving via World Bank Loan for Fushun WSC
Categories/Status | 2016 | Energy Saving | 2022
Total Savinging, kW-h | 4650800 | 693948 | 3956852 | Categories / WSCs | Anshan | Fushun | Fuxin | Gaizhou | Shenyang
Water Intake Pumping | 2341000 | 342436 | 1998564 | Total Water Saving, m3/year | 3146482.5 | 17509725 | 4791136 | 604440 | 4891097.82 | 0.91 | 类别 / 水公司 | 鞍山 | 抚顺 | 阜新 | 盖州 | 沈阳
Produced Water Pumping | 1281500 | 123689 | 1157811 | Total Saving, RMB/year | 2863299.075 | 15933849.75 | 4359933.76 | 550040.4 | 4450899.0162 |  | 总节水, m3/年 | 3146482.5 | 17509725 | 4791136 | 604440 | 4891097.82
Distribution Pumping | 635800 | 86023 | 549777 | Total Investment, RMB | 51636200 | 360870000 | 66360000 | 122380000 | 71400000 |  | 总节水费, RMB/年 | 2863299.075 | 15933849.75 | 4359933.76 | 550040.4 | 4450899.0162
Secondary Booster Pumping | 392500 | 141800 | 250700 | Total Energy Saving, kWh/year | 1152960 | 1701600 | 724560 | 178008 | 1938000 |  | 工程造价, RMB | 51636200 | 360870000 | 66360000 | 122380000 | 71400000
Others | 0 | 0 | 0 | Energy Cost, RMB/kW-h | 0.71 | 0.66 | 0.75 | 0.8 | 0.72 |  | 总节能, kWh/年 | 1152960 | 1701600 | 724560 | 178008 | 1938000
|  |  |  | Total Saving, RMB/year | 818601.6 | 1123056 | 543420 | 142406.4 | 1395360 |  | 平均电价, RMB/kW-h | 0.71 | 0.66 | 0.75 | 0.8 | 0.72
Energy Saving via World Bank Loan for Fuxin WSC |  |  |  | Total Investment, RMB | 29900000 | 33220000 | 2750000 | 4597500 | 44520000 |  | 总节电费, RMB/年 | 818601.6 | 1123056 | 543420 | 142406.4 | 1395360
Categories/Status | 2016 | Energy Saving | 2022 | [7 empty] | 工程造价, RMB | 29900000 | 33220000 | 2750000 | 4597500 | 44520000
Total Savinging, kW-h | 4831106 | 472208 | 4269716
Water Intake Pumping | 2749512 | 288059 | 2461453
Produced Water Pumping | 992648 | 94302 | 898346 | 小区管道改造节水, m3/年
Distribution Pumping | 282684 | 29467 | 253217 | 类别 / 水公司 | 鞍山 | 抚顺 | 阜新 | 盖州 | 沈阳
Secondary Booster Pumping | 806262 | 60380 | 656700 | 小区改造数，个 | 28 | 271 | 48 | 41 | 63
Others | 0 | 0 | 0 | 小区管道改造节水，案例 | 2576535 | 23881887.95 | 5110000 | 3108705 | 5585278.6667
|  |  |  | 小区管道改造节水，汇总 | 3146482.5 | 17509725 | 4791136 | 604440 | 4891097.82
Energy Saving via World Bank Loan for Gaizhou WSC |  |  |  | 差额 | -569947.5 | 6372162.95 | 318864 | 2504265 | 694180.8467
Categories/Status | 2016 | Energy Saving | 2022
Total Savinging, kW-h | 456411 | 14834 | 441577 | 二次加压泵站改造节能，kW-h/年
Water Intake Pumping | 206870 | 0 | 206870 | 类别 / 水公司 | 鞍山 | 抚顺 | 阜新 | 盖州 | 沈阳
Produced Water Pumping | 207201 | 0 | 207201 | 二次加压泵站改造数，站 | 80 | 70 | 9 | 14 | 99
Distribution Pumping | 0 | 0 | 0 | 二次加压泵站节能，案例 | 1079436 | 1700760 | 167424 | 178008 | 2633592
Secondary Booster Pumping | 42340 | 14834 | 27506 | 二次加压泵站节能，汇总 | 1152960 | 1701600 | 724560 | 178008 | 1938000
Others | 0 | 0 | 0 | 差额 | -73524 | -840 | -557136 | 0 | 695592
Power Usage and Energy Saving via World Bank Loan for Shenyang WSC
Categories/Status | 2016 | Energy Saving | 2022
Total Savinging, kW-h | 28310000 | 498421 | 27811579
Water Intake Pumping | 4500000 | 0 | 4500000
Produced Water Pumping | 12510000 | 336921 | 12173079
Distribution Pumping |  |  | 0
Secondary Booster Pumping | 11300000 | 161500 | 11138500
Others | 0 | 0 | 0